## Slide 1
ACO Haustechnik Grease separators - planning Matthias Jäger Product Management
Grease Separators & Process Engineering

## Slide 2: DIMENSIONING

## Slide 3: Regulations for Grease Separators
EN 1825-1
Manufacture standard
EN 1825-2
Application standard
Dimensioning
Installation
Maintenance
Manufacturing principles
and testing of
grease separators

## Slide 4: Dimensioning: Determination of Nominal Size
Inlet: Volume rate in l/s determines the nominal size of the grease separator

## Slide 5
Dimensioning (EN 1825)
European Standard
Types of dimensioning the grease separator
Based on kitchen equipment
Based on meals per day
Based on number of slaughtered animals

## Slide 6: Dimensioning (EN 1825) European Standard
FLOW RATE (l/s)
NOMINAL SIZE (NS)
Based on kitchen equipment
Based on meals per day
Based on number of slaughtered animals
DIFFICULTY FACTORS

## Slide 7: Examples of Dimensioning
Inlet:
Determined Volume rate
2,85 l/s
Inlet:
Determined Volume rate
4,8 l/s
Inlet:
Determined Volume rate
9,3 l/s
Nominal size 3
Nominal size 5,5
Nominal size 10

## Slide 8: Headline, Verdana Fett 20 P. Maximal zwei Zeilen. Zeilenabstand 1,1 Zeilen.
1.) Sizing according to produced meals per day
Notes: 8

## Slide 9: Dimensioning according to meals per day
Type of kitchen
Quantity of produced meals per day
Operating hours
Factors:

## Slide 10: Types of kitchen
EN 1825 defines specific water consumption per warm meal for:
Hotels | Speciality Restaurants | Works‘ kitchen/ refectories | Hospitals | All day large scale kitchens

## Slide 11: Type of kitchen
Example: 8 operating hours and 200 meals per day
Hotels | Speciality Restaurants | Works‘ kitchen/ refectories | Hospitals | All day large scale kitchens
Chart: 
| Hotel | Speciality Restaurant | Work's kitchen/refectory | Hospital | All day large scale kitchen
 | 3.4722 | 2.9514 | 0.69444 | 1.8056 | 1.5278
l/s

## Slide 12: Produced meals per day
According to the formular used in EN 1825, increasing amount of produced meals perday increases the maximum wastewater inflow.

## Slide 13: Produced meals per day
Example: 8 operating hours in a hotel kitchen
Chart: 
| 50 | 100 | 150 | 200 | 300 | 500 | 700 | 1000
Maximum wastewater inflow (l/s) | 0.86806 | 1.7361 | 2.6042 | 3.4722 | 5.2083 | 8.6806 | 12.1528 | 17.3611
Maximum wastewater inflow (l/s)
Produced meals per day

## Slide 14: Operating hours
According to the formular used in EN 1825, an increasing amount of operating hours decreases the maximum wastewater flow at fixed other conditions (type of kitchen, meals per day)

## Slide 15: Operating hours
Example: Hotel kitchen, 200 meals per day
Maximum wastewater inflow (l/s)
Operating hours per day
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Maximum wastewater inflow (l/s) | 27.7778 | 13.8889 | 9.2593 | 6.9444 | 5.5556 | 4.6296 | 3.9683 | 3.4722 | 3.0864 | 2.7778 | 2.5253 | 2.3148 | 2.1368 | 1.9841 | 1.8519 | 1.7361 | 1.634 | 1.5432 | 1.462 | 1.3889 | 1.3228 | 1.2626 | 1.2077 | 1.1574

## Slide 16: Headline, Verdana Fett 20 P. Maximal zwei Zeilen. Zeilenabstand 1,1 Zeilen.
Difficulty factors
Notes: 16

## Slide 17: Types of Difficulty factors
According to EN 1825 there exits THREE different difficulty factors:
Cleaning Agents
Temperature
Density of grease
All these factors reduce the separation effect

## Slide 18: Difficulty factor: Cleaning Agents
Application of difficulty factor for cleaning agents according to
EN 1825:
Application of cleaning agents | Difficulty factor
No application | 1,0
Application in commercial kitchens | 1,3
Application in hospitals | 1,5

## Slide 19: Difficulty factor: temperature
Application of difficulty factor for temperature according to EN 1825:
Temperature of kitchen wastewater | Difficulty factor
Below 60 °C | 1,0
Above 60 °C | 1,3

## Slide 20: Difficulty factor: density of cooking oil
Application of difficulty factor for density according to EN 1825:
Density of grease or oil | Difficulty factor
Up to 0.94 g/cm3 | 1,0
Above 0.94 g/cm3 | 1,3

## Slide 21
160 Meals per day
6 kitchen operating time
Type of kitchen: Hotel
Density of grease: > 0,94 g/cm³
Inlet temperature < 60°C
Use of cleaning agents: yes
Example: Meals per day
Dimensioning according to EN 1825

## Slide 22
Useful Remarks:
Further Information
No information about the meals per day ?
Maybe you can get some information about the amount of seats !

## Slide 23
Useful Remarks:
Further Information
No information about the
density of the grease ?
EN 1825-2 appendix B includes table with density values of selected fats
and oils.

## Slide 24: Headline, Verdana Fett 20 P. Maximal zwei Zeilen. Zeilenabstand 1,1 Zeilen.
2.) Sizing according to kitchen equipment
Notes: 24

## Slide 25: Dimensioning according kitchen equipment
Type of equipment
Quantity of each specific equipment
Factors:

## Slide 26: Dimensioning according to kitchen equipment
EN 1825 defines qi value and factors for simultanous operation:
Rinse sinks | Dish washers | Tilting frying pans | Tilting boiling pans

## Slide 27: Dimensioning according to kitchen equipment
Example: Tilting boiling pan, outlet with 100 mm, 4 items
= 2,52 l/s

## Slide 28: Headline, Verdana Fett 20 P. Maximal zwei Zeilen. Zeilenabstand 1,1 Zeilen.
Selection of Nominal Sizes (NS)
Notes: 28

## Slide 29
Useful Remarks I:
Further Information
Grease and sludge will become hard during the „saved“ weeks.
NS 4
NS 10
According to calculation you
need a NS 4 but…
…you choose NS 10 to delay
disposal time

## Slide 30
Useful Remarks II:
Further Information
>NS 20 manunfactured from PE plates (welded)
>NS 20 manunfactured from stainless steel

## Slide 31
We also offer Nominal Sizes 3, 5.5 and 8.5.
May be you can quote against a competitor that doesn‘t offer that sizes 
NS | 1 | 2 | 3 | 4 | 5.5 | 7 | 8.5 | 10 | 15 | 20
 |  |  | X |  | X |  | X |  |  | 
Competitors |  |  |  |  |  |  |  |  |  | 
Useful Remarks III:
Further Information

## Slide 32: Headline, Verdana Fett 20 P. Maximal zwei Zeilen. Zeilenabstand 1,1 Zeilen.
Further questions ?
Notes: 32