## Slide 1: ACO ShowerDrain
Modern and Efficient Drainage for Shower Areas Stadtlengsfeld, 22th September 2016

## Slide 2: Overview
History and Customer Needs
Product Standards and Installation Requirements
ACO ShowerDrain Product Portfolio
Innovations for Tomorrow

## Slide 3: Evolution – History of Bathrooms
1966
2006
1985
13. Jh.
1850
2000 v. Chr.

## Slide 4
ACO ShowerDrain – Today‘s Market Presence – Competitors

## Slide 5
ACO ShowerDrain - today
Market presence
ACO ShowerDrain - Today‘s Market Presence

## Slide 6: Areas of Application Daily Use
Actual Situation: Renovation holdup
Outdated Shower places with High Entry Barrier

## Slide 7: Areas of Application Universal Design
Flexibility for Use
Simple and Intuitive Operation
Minimized Physical Effort
Result = Usability for all + Design

## Slide 8: Areas of Application Demographic Shift
Senior homes, Senior residences
Hospitals, Rehab facilities
SPA, Wellness resorts, Gyms, Sport facilities
Hotels, Recreational areas, Service areas
Private residential buildings

## Slide 9: Overview
History and Customer needs
Product Standard and Installation Requirements
ACO ShowerDrain Product Portfolio
Innovations for Tomorrow

## Slide 10: Product norm EN 1253 Product scope
  Norm for floor and roof gullies. Shower channels were not included
  Part 1 = Requirements with and without foul air trap (FAT)
  Part 2 = Testing procedures with and without foul air trap (FAT)
  Floor gullies with foul air trap include shower channels
  Part 1 = Gullies with 50 mm foul air trap (FAT)
  Part 2 = Gullies without foul air trap (FAT) (e.g. roof gullies)
Old
New

## Slide 11: Product norm EN 1253 Temperature cycle test
  A test procedure to check the performance of the product under different water temperatures
  Differentiation of testing accoding to scope of application
    class A: 1500 cycles  all applications
    class B: 360 cycles  Private bath rooms (DN 32 to DN 75)
Old
New

## Slide 12: Product norm EN 1253 Temperature cycle test
Temperature cycle test for products acc. to class A with 1500 cycles class B with 360 cycles
1
2
3
4
  60 s: 93°C hot water 0,5 l/s
  60 s: Pause
  60 s: 15°C cold water 0,5 l/s
  60 s: Pause
  One cycle includes:
New

## Slide 13: Product norm EN 1253 Slope for outlet spigot
  Pipe running from the outlet spigot shall be isntalled with 2% slope against horizontal line
  Pipe running from the outlet spigot shall be isntalled with 1,5% slope against horizontal line
Old
New

## Slide 14: Product norm EN 1253 Flanges
  No definition for flanges in combination with fluid sealing systems (e.g. thin bed sealing)
  Effective minimal flange width 30mm for adhesive flange to apply fluid sealing systems or glued sealing membranes
Old
New

## Slide 15: Product norm EN 1253 Loading test
  Standardized test blocks for gullies and channels
  4 clear openings: <140, 140–200, 200–300, >300
  No unsupported distance between test block and edge of grating defined
Old
New
  Round test blocks for gullies, rectangular test blocks for channels
  6 clear openings: 25–50, 50–90, 90–140, 140–200, 200–300, >300
  Unsupported distance between test block and edge of grating defined
300

## Slide 16: Product norm EN 1253 Apertures in gratings (holes, slots)
  Acceptable apertures for bare feet area between 6 and 8mm
  No definition for apertures inside slot channels
  Acceptable apertures for bare feet area between 4 and 8mm
  Apertures may also be between grating and frame (slot drainage)
Old
New

## Slide 17: Installation Requirements Slope and Flow rates
  Slope in 4 directions needed for floor gullies

## Slide 18: Installation Requirements Slope and Flow rates
  Design examples for Floor gullies

## Slide 19: Installation Requirements Slope and Flow rates
  Slope in one direction for shower channels
at the wall
inside the room

## Slide 20: Installation Requirements Slope and Flow rates
  Design examples for shower channels

## Slide 21: Installation Requirements Slope and Flow rates
  For location at the wall water stacking is technically possible
  0.4 l/s (no water stacking)
  0.6 l/s (water head acc. to EN 1253-1, 20 mm),
    (must be min. 0.4 l/s)
Slope approx. 1.5 %
Slope approx. 1.5 %

## Slide 22: Installation Requirements Slope and Flow rates
  0.4 l/s (no water stacking)
  Water head acc. to EN 1253-1 not possible
  For location inside the room water stacking is technically not possible
Slope approx. 1.5 %
Slope approx. 1.5 %

## Slide 23: Installation Requirements Slope and Flow rates
Head shower Rain Sky
  Flow rates of shower installations
  approx. 22 l/min. at 3 bar
  0.37 l/sec.
  approx. 18 l/min. at 3 bar
  0.30 l/sec.
  > 0.4 l/ sec.
Hand shower
Head shower

## Slide 24: Installation Requirements Slope and Flow rates
  Interface between shower head and shower channel
24 l/min = 0.4 l/ s
Water stacking a. grating
0 mm
5 mm
15 mm
Number of gullies
1 gully
2 gullies
3 gullies
0.4 l/s
0.7 l/s
1.0 l/s
0.5 l/s
0.8 l/s
1.25 l/s
0.6 l/s
1.0 l/s
1.4 l/s

## Slide 25: Installation Requirements Design and Dimensions
  Installation height: standard FAT acc. to EN1253
  (e.g.: ACO ShowerDrain E)
Building height 90 mm (1)
Installation height 105 mm (2)
Adjustability + 55 mm (3)
Foul air trap 50mm acc. to EN 1253 part 1
(1)
(2)
(3)

## Slide 26: Installation Requirements Design and Dimensions
  Installation height: renovation solution (e.g.: ACO ShowerDrain E)
Building height 64 mm (1)
Installation height 79 mm (2)
Adjustability + 55 mm (3)
Foul air trap 25 mm
(1)
(2)
(3)

## Slide 27: Installation Requirements Noise Protection

## Slide 28: Installation Requirements Noise Protection
Highest noise requirements are standard for
ACO ShowerDrain
  Celestial peace: German noise guidelines
DIN 4109, A1 – noise protection in buildings
≤ 30 dB
VDl 4100, SSt – noise protection in residential buildings, (higher requirements)
≤ 22 dB

## Slide 29: Installation Requirements Fire Protection

## Slide 30: Installation Requirements Fire Protection
Fire is an extremelly dangerous incident according to civil and public law.
National laws require to take prevent actions in order to avoid catastrophies.
National laws maybe detailed on regional level by specific:
Fire and rescue regulations
Building regulations related to fire protection

## Slide 31: Installation Requirements Fire Protection
Target
  The Product Solution
After 120 min. ≤ 180 °C
No smoke or fire passage
Acc. to German fire class R 120
All grating designs maybe used
Enable rescue
Provide escape route
Gain time

## Slide 32: Installation Requirements Fire Protection
  … in order to avoid this incident.
Smoke and fire passage to upper floor, when using vertical shower channels or gullies without fire protective solution
Vertical shower channel without fire protective solution

## Slide 33: Overview
History and Customer needs
Product Standards and Installation Requirements
ACO ShowerDrain Product Portfolio
Innovations for Tomorrow

## Slide 34: ACO ShowerDrain Plattform & Product portfolio*
Best
Good
*In addition: customized+special shower channels (i.e. ShowerDrain X)
ACO ShowerDrain C
The functional channel
ACO ShowerDrain B
The basic channel
Better
ACO ShowerDrain E
The versatile channel
ACO ShowerDrain S
The elegant channel

## Slide 35: ACO ShowerDrain product portfolio ACO ShowerDrain E
Flow rates
  No water stacking: 0.4 l/s
  With stacking (20 mm): 0.6 l/s
Building - installation height
  64-79 mm ND40 WS25
  90-105 mm ND50 WS50
Floor sealing
  Fully welded gully body
  Fully integrated 30mm steel flange
Handling
  Feet pre-installed
  One-piece product solution
Length
  700/ 800/ 900/ 1000/ 1200 mm

## Slide 36: ACO ShowerDrain product portfolio ACO ShowerDrain E – fire protection
Flow rates
  No water stacking: 0.5 l/s
  With stacking (20 mm): 0.65 l/s
Building - installation height
  64-79 mm ND40 WS25 (Fit-in)
  90-105 mm ND50 WS50 (no Fit-in)
Floor sealing
  Fully welded gully body
  Fully integrated 30mm steel flange
Handling
  Easy vertical installation by core bore and Fit-in
  One-piece product solution
Length
  700/ 800/ 900/ 1000/ 1200 mm

## Slide 37: ACO ShowerDrain product portfolio ACO ShowerDrain E – variety & individuality
Grating
Length
Flange
Gully
max. 2400 mm
Safety
Accessor.
  In Addition:
  Customized frame height for natural stone/ marble (16-30 mm)
  Individual Logos
Max. 3 (flow rate up to 1.4 l/s),
Individual position

## Slide 38: ACO ShowerDrain Produkt Portfolio RUG Self Comfort
Length
  800/ 900/ 1000 mm
Flow rate
  No water stacking: 0.35 l/s
  With stacking (20 mm): 0.55 l/s
Building - installation height
  Shark: 123 (108) mm ND 40/50
  Twist: 101 (86) mm ND 40/50
Floor sealing
  Rotateable gully (360°)
  Fully integrated 30mm steel flange
Handling
  Feet pre-installed, height-adjustable
Shark Comfort
Twist Comfort

## Slide 39: ACO ShowerDrain Product Portfolio ACO ShowerDrain C
Flow rates
  No water stacking: 0.5 l/s
  With stacking (20 mm): 0.9 l/s
Building - installation height
  53-65 mm ND40 WS30
  80-92 mm ND50 WS50
Floor sealing
  Fully welded gully body
  Fully integrated 30mm steel flange
Handling
  Concrete anchors / flaps
  One-piece product solution
Length
  558/ 685/ 785/ 885/ 985/ 1185 mm

## Slide 40: ACO ShowerDrain Product Portfolio ACO ShowerDrain C customized
Grating
Length
Flange
Gully
min. 400 mm
Max. 3 pieces
max. 2200 mm
  In Addition:
  Surface treatment
  Coated flange
  Anchor or height-adjustable feet

## Slide 41: ACO ShowerDrain Product Portfolio ACO ShowerDrain B
Flow rates
  No water stacking: 0.35 l/s
  With stacking (20 mm): 0.55 l/s
Building - installation height
  87 mm ND 40/50 WS 25 mm
Floor sealing
  Rotateable gully
  Fully integrated 30mm steel flange
Handling
  Concrete anchors / flaps
Length
  685/ 785/ 885/ 985 mm
ACO ShowerDrain B
RUG Self Shark Standard

## Slide 42: ACO ShowerDrain Product Portfolio ACO ShowerDrain S
Flow rates
  No water stacking: 0.35-0.50 l/s
  With stack.(20 mm): 0.55-0.80 l/s
Building height
  55 mm ND32/40 WS25
  64 mm ND40 WS34
  80 mm ND50 WS50
Floor sealing
  Fully welded gully body
  Fully integrated 30mm steel flange
Handling
  Feet pre-installed
  One-piece product solution
Length
  700/ 800/ 900/ 1000/ 1200/ 1500 mm
  From 1000 mm: 2 gullies
Plate
Stripes

## Slide 43: ACO ShowerDrain Product Portfolio ACO ShowerDrain S
Scope of delivery:
1 grating
4 different feet
  H= 11, 14, 16 or 22 mm
On site adjustment to the height of tiles

## Slide 44: ACO ShowerDrain Product Portfolio ACO ShowerDrain S

## Slide 45: ACO ShowerDrain Product Portfolio Strategy
Good
Better
Best
Sanitary
wholesale
DIY
Builder’s Merchants
B
C
E / S
B
C
E / S
RUG Self Comfort
RUG Self Standard
?
http://www.rug-self.com/files/RUG_Self_Ablaeufe_2015_rus.pdf

## Slide 46: ACO ShowerDrain Product Differentiation
Shower Channel
Gully
Flange
Grating
Fixation
Length
Material steel
or plastic
Pre assembled (water tight)
Access to piping
Material plastic
rotatable
Width
30 mm
Steel
Coated
Wall version
Width 30 mm
Steel
Wall version
Width 30 mm
Steel/Plastic
Steel (>5)
Tile grating
Glass grating
Steel 5 designs
Tile grating
Steel/ Plastic
Adjustable feet
Steel anchors (flaps)
Standard + Customizing
Fixed sizes 700 – 1200 mm
Fixed sizes 700 –
900 mm
Material steel
Welded
Access to
piping
FAT 2 heights
No fixation
Options
Surface
Light
Multiple gullies
Noise-Stop
Fire-Stop
Smell-Stop
Noise-Stop
No options
Electro pol.
Grinded
Pickle passivated
Plastic, not coated
Best
Better
Good

## Slide 47: ACO ShowerDrain Product Portfolio ACO ShowerStep/ RUG Self Profilschiene
Surface treatment
  Electro-polished
  Grinded
Version
  Left
  Right
Tile thickness
  10 mm
  12,5 mm
  15 mm
Length
  990 mm
  1490 mm
  Individual cutting on site
  RUG Self: only 15 mm, gebürstet available
  Glass wall can be installed on ShowerStep
Notes: 12 mm width  installation Glaswall

## Slide 48: Overview
History and Customer needs
Product Standards and Installation Requirements
ACO ShowerDrain Product Portfolio
Innovations for Tomorrow

## Slide 49: ACO ShowerDrain Strategic Meeting Agenda
ShowerDrain X

## Slide 50: ACO ShowerDrain X

## Slide 51: ACO ShowerDrain X
Less warm drinkable water is needed to heat up the showering water
38 % Efficiency

## Slide 52
10°C
20°C
60-70°C
10°C
60-70°C
ACO ShowerDrain X

## Slide 53
https://www.youtube.com/watch?v=saPTsi-OZac
ACO ShowerDrain X

## Slide 54: ACO ShowerDrain Strategic Meeting Agenda
ShowerDrain
Walk-in

## Slide 55: ACO Walk-in Therm Grating Coal

## Slide 56: ACO Walk-in Therm Grating Timber

## Slide 57: Therm Gratings Material
WPC – Wood Plastic Composite
 Thermoplastic processed material
65% wood fibre
35% polymer
UV resistant
Chlorine water resistant
Salt water resistant
Splinter proof
Wooden feel of surface

## Slide 58: ACO Walk-in System Overview
Application
1
Design
3
Gully
4
Size
2
700 x 500 mm
800 x 500 mm
900 x 500 mm
1000 x 500 mm
1200 x 500 mm

## Slide 60: ACO ShowerDrain Strategic Meeting Agenda
ShowerDrain
Lightline Pro

## Slide 61: ACO Lightline Pro

## Slide 62: ACO Lightline Pro

## Slide 63: ACO Lightline Pro

## Slide 64: ACO Lightline Pro Product Information
Pre-manufactured stainless steel channel with integrated LED lights
Stainless steel 1.4301, e-polished
Installation height 10 mm (for integration into tiled floor)
Width 15 mm
Available lengths 700 to 1200 mm
Light options
  Neutral white (4.000 K)
  Cold white (6.000 K)

## Slide 65: ACO Lightline Pro Details
Suitable for barefeet- and wet areas (Area 0 acc. to DIN VDE 0100-701)
Protective class IP 68 (DIN 40050)
Connected cable 5 m
For combination with mains adapter 24V, DC (scope of delivery)
Life time until 80% luminance: >40.000 h
  Equals 55 years based on 2h operations per day

## Slide 66
Free integration into the floor
Installation independent of a channel
Handling via a light switch

## Slide 67: ACO ShowerDrain Strategic Meeting Agenda
ACO ShowerDrain W

## Slide 68: ACO ShowerDrain W – Netherlands Drainage into the Wall

## Slide 69: ACO ShowerDrain Strategic Meeting Agenda
ACO ShowerDrain
Sales support

## Slide 70: ACO ShowerDrain Sales Support
ACO ShowerDrain display
ACO ShowerDrain sales stand
ACO ShowerDrain sample case

## Slide 71: International Sales Support Installation Video
https://www.youtube.com/watch?v=uKl-EE23N2k

## Slide 72: ACO ShowerDrain Sales Support
Online Design Configurator
http://app.aco-haustechnik.de/badkonfig/konfigurator_en.html